## Sheet1
Test File Name
Device: | Machine A89E03
S/N: | 12345678 |  |  |  | VID: | P3U30-200090360
Program version: |  |  | V30.207
HW version: |  |  | 1.2
Order code: |  |  | 6AAA1BCAA
Auxiliary power: |  |  | 48 - 230 Vac/dv |  |  | REL52022
Nominal inputs current: |  |  | In: 1/5A lo1n: 1/5A
Nominal inputs voltage: |  |  | 100/110V
Frequency: |  |  | 50/60Hz
Auxiliary power: |  |  | Voltage | Current | Power ( < 15W )
|  |  | 111 Vdc | 56.54 mA | 6.29 W
Communication: |  | Local (front)
|  | Remote |  |  | 2 x RJ-45-Interface
Ethernet (MAC 001AD34183FF)
Digital inputs: |  |  |  |  | ( Connectors: X3:3-6, X4: 1-1.4, X5: 1-8 )
Output relays: |  |  |  |  | ( Connectors: X3: 7-20, X5:9-14 )
Insulation Test: |  |  |  |  | ( IEC 60255-27 2kV, 50Hz )
Meas. Accuracy: |  | CT = 5000 A / 5 A (In = 5 A)
CTo = 500 A / 5 A (In = 5 A) or 100 A / 1 A (In = 1 A)
VT1000/100V f=50Hz
Current channels: |  |  | Channel | Supply value | Measured | Error | Tolerance
|  | 0.1 x In | IL1 | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | IL2 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | IL3 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  | 1.0 x In | IL1 | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | IL2 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | IL3 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  | 4.0 x In | IL1 | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | IL2 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | IL3 | 0.5002 A | 500 A | -0.04 % |  | Pass
Residual current: |  |  | Channel | Supply value | Measured | Error | Tolerance
|  | 0.1 x In | In = 1 A | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | In = 1 A | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | In = 1 A | 0.5002 A | 500 A | -0.04 % |  | Pass
|  | 1.0 x In | In = 1 A | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | In = 1 A | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | In = 1 A | 0.5002 A | 500 A | -0.04 % |  | Pass
Voltage channels: |  |  | Channel | Supply value | Measured | Error | Tolerance
Mode: 3LN/LNy |  | 0.02 x Un | IL1 | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | IL2 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | IL3 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  | 0.1 x Un | IL1 | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | IL2 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | IL3 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  | 1.0 x Un | IL1 | 0.5002 A | 500 A | -0.04 % | ± 2.5% | Pass
|  |  | IL2 | 0.5002 A | 500 A | -0.04 % |  | Pass
|  |  | IL3 | 0.5002 A | 500 A | -0.04 % |  | Pass
Power & Frequency: |  |  | Channel | Supply value | Measured | Error | Tolerance
|  |  | P | 0.5002 A | 500 A | -0.04 % | ± 20% | Pass
|  | 1.00 x In | Q | 0.5002 A | 500 A | -0.04 % | ± 20% | Pass
|  | 1.00 x Un | S | 0.5002 A | 500 A | -0.04 % | ± 20% | Pass
|  | 50Hz | P.F. | 0.5002 A | 500 A | -0.04 % | ± 20% | Pass
|  |  | f | 0.5002 A | 500 A | -0.04 % | ± 20% | Pass
Functional Test
Stage | Delay type | I > | Tp | Input | Measured | Error | Tolerance
I > | NI | 0.5 pu | 0.10 | 0.620 pu | 3.345 s | 0.098 s | ±5% | Pass
Stage | Delay type | I > | t > | Input |  | Error | Tolerance
IDir > | DT | 0.5 pu | 0.10 | 0.620 pu | 3.345 s | 0.098 s | ±5% | Pass
I >> | DT | 1.0 pu | 0.11 | 0.621 pu | 3.346 s | 0.099 s |  | Pass
Io > | DT | 2.0 pu | 0.12 | 0.622 pu | 3.347 s | 0.100 s |  | Pass